Electrical Work Plan
(Reference ES&H Bulletin 68A. Attach additional pages as needed)
Job Name:
   White Circuit Pulser Enclosure Access SAPE/ELP - 043  

Location:
   B140 and 2MVA Transformer on West side of B140 

Effective Dates Of Plan -  Start:
   12/16/04

End:
   12/16/05

Work To Be Performed By:
  Critt Taylor, Ray Ortiz, Greg Johnson, John Wachter

Person In Charge:   Fernando Rafael

Phone:
   4607

Description Of Work:
Perform SAPE/ELP 043 “White Circuit Pulser Enclosure” 
This procedure defines the removal of DC power and discharging electrical hazards in the White Circuit Pulser Enclosure.  The Copley, Bias and Pulser supplies are isolated to prevent possible feed back to the White Circuit. The 12 kV vacuum breaker operated provides power to the Bias, Pulser, and B2-B6 supplies therefore the B2-B6 power supply will also be shut down for access to the White Circuit Enclosure
Associated Hazards (e.g. voltage, current, etc.):
For a nominal system voltage range, 751 to 15000 volts, the Restricted Approach Boundary is 2 foot 2 inches per NFPA 70E Table 130.2(C). A Flash Protection Boundary of 3 inches was calculated for the 480 kW supplies and the pulser capacitor and 1 inch for the remaining supplies. 
Hazard Mitigation (e.g. specific PPE, barriers, etc):
Follow Precautions and PPE requirements in SAPE/ELP 043 “White Circuit Pulser Enclosure.”
The 12 kV Vacuum Breaker shall be opened prior to operating the 480 V breakers for the Bias and Pulser power supplies to allow the use of Hazard/Risk Category 0 PPE when operating the PDP Panel 480 V breakers. 
Inspection Required After Work?  -  Yes
 
 
No 
X

(Required for New Installations.)
Originator:
Rafael

Date:
 12/08/04  

Approvals As Required By Bulletin 68a (Sign, print name and title, and date):

Participants (All workers to read, sign, print name and date): 
November 12, 2004
SLAC-I-730-0A11R-002
Electrical Work Plan, Page 1 of 1

