Electrical Work Plan
(Reference ES&H Bulletin 68A. Attach additional pages as needed)
Job Name:
SPEAR3 Large Power Supplies Control Board Troubleshoot and Inspection

Location:
   B118 – Power Supplies Build

Effective Dates Of Plan -  Start:
   03/04/2005

End:
   03/03/2006

Work To Be Performed By:
  
Fernando Rafael, Greg Johnson and Critt Taylor

Person In Charge:   Fernando Rafael

Phone:
   x4607

Description Of Work:
Troubleshoot, inspect and test SPEAR3 Large Power Supplies System.

Including:

· Lock and Tag pertaining Power supply, using the appropriate ELP and Lock and Tag MCC-3 or MCC-4, as required.
· Verify Power Supply de-energization, measuring the voltage in 480 Vac bus and output DC bus.
· Access the power supply through the back door using key #IN8

· Use voltmeter class IV or high, rated 25 kV.

· Ground the output busses using appropriate ground hook
· Turn Auxiliary Breaker off and verify absence of voltage 120 Vac and output voltage +/- 15 Vdc and 24 Vdc, using class 3 voltmeter in the Auxiliary supplies.
· Troubleshoot the power supply using Unipolar Large Switchmode DC Power Supply manual, reference Number JO4958/4959 – IEPOWER Manual.

Associated Hazards (e.g. voltage, current, etc.):
· 480 Vac Input Voltage
· 120 Vac AC controls

· 600 Vdc output voltage (storage energy in output CAP’s)
Hazard Mitigation (e.g. specific PPE, barriers, etc):
Lock Out the system using appropriate ELP Procedure.
Use PPE to turn Breakers:
· Hazard Risk Category 0 clothing, non-melting, flammable materials, (i.e. untreated cotton, wool, rayon, or silk, or blends of these materials) Shirt (long sleeve), pants (long), closed toe work shoes.

· Electrical safety glasses/goggles w/UV Protection
· Two Person Rule, both CPR training
Inspection Required After Work?  -  Yes
 
 
No 


(Required for New Installations.)
Originator:
Fernando Rafael

Date:
   01/23/2005

Approvals As Required By Bulletin 68a (Sign, print name and title, and date):

Participants (All workers to read, sign, print name and date): 
November 12, 2004
SLAC-I-730-0A11R-002
Electrical Work Plan, Page 1 of 2

