Electrical Work Plan
(Reference ES&H Bulletin 68A. Attach additional pages as needed)
Job Name:
   Service Power Supplies Racks and Cabinet in B118

Location:
   B118 and B140

Effective Dates Of Plan -  Start:
   03/16/2005

End:
   03/15/2006

Work To Be Performed By:
  
Fernando Rafael, Greg Johnson and Critt Taylor

Person In Charge:   Fernando Rafael

Phone:
   x4607

Description Of Work:
Service and maintain power supplies racks and cabinets in B-118 and B140.
The work includes:
· Troubleshoot and repair Power Supplies 480/208/120 VAC distribution INSIDE the rack

· Troubleshoot and repair Power Supplies control cables

· Lock and Tag applicable rack or cabinet using appropriate PPE. 
· Voltage Verification using rated Voltmeter or applicable procedure.
· Verify torque in cables bolts and nuts.
· Replace damaged terminations, bolts, sensors (including Klyxon and smoke detectors)
· Clean and replace fans
Associated Hazards (e.g. voltage, current, etc.):
3 phase 480 VAC Input
3 phase 208 VAC Input

120 Vac Input

Combination of up to 1200 Vdc and 800 A Output. 

Storage energy in CAP bank.
Hazard Mitigation (e.g. specific PPE, barriers, etc):
Use applicable procedure for test.
· Two person rule.
· Lock Out the system using appropriate ELP Procedure.

· Never approach the restrict Approach Boundary define in NFPE-70E Table 130.2(2) until the voltage absence has been verified using appropriate SAPE/ELP.

· Use PPE:
-  Hazard Risk Category 0 clothing, non-melting, flammable materials, (i.e. untreated cotton, wool, rayon, or silk, or blends of these materials) Shirt (long sleeve), pants (long), closed toe work shoes.

-  Electrical safety glasses/goggles w/UV Protection
-  Gloves
Inspection Required After Work?  -  Yes
 
 
No 
X

(Required for New Installations.)
Originator:
Fernando Rafael

Date:
   03/16/2005

Approvals As Required By Bulletin 68a (Sign, print name and title, and date):

Participants (All workers to read, sign, print name and date): 
November 12, 2004
SLAC-I-730-0A11R-002
Electrical Work Plan, Page 1 of 2

