Electrical Work Plan
(Reference ES&H Bulletin 68A. Attach additional pages as needed)
Job Name:
   SPEAR Tunnel Access Hazards Verification 

Location:
   SPEAR Tunnel, B118, B132-101, B514

Effective Dates Of Plan -  Start:
   12/08/04

End:
   12/08/05

Work To Be Performed By:
  Critt Taylor, Ray Ortiz, Greg Johnson, John Wachter

Person In Charge:   Fernando Rafael

Phone:
   4607

Description Of Work:
Perform SAPE 111 “SPEAR Tunnel Access Hazards Verification Procedure”
This procedure describes the steps necessary to “manually” verify that all SPEAR Ring hazards are in a de-energized condition to allow entry into the SPEAR tunnel, when the normal verification process is not possible

Associated Hazards (e.g. voltage, current, etc.):
String magnet voltages 600 to 700 V DC
Individual magnet voltages 100 to 200V DC
Hazard Mitigation (e.g. specific PPE, barriers, etc):
Follow Precautions and PPE requirements in SAPE 111 “SPEAR Tunnel Access Hazards Verification Procedure”
Note: For a nominal system voltage range, phases to phase, of 301 to 750 volts, the Restricted Approach Boundary is 1 foot 0 inches per NFPA 70E Table 130.2(C). A Flash Protection Boundary of 1 inch was calculated for the worst case, the Dipole Bulk supply.  The others have lower stored energy.
Inspection Required After Work?  -  Yes
 
 
No 
X

(Required for New Installations.)
Originator:
Rafael

Date:
 12/08/04  

Approvals As Required By Bulletin 68a (Sign, print name and title, and date):

Participants (All workers to read, sign, print name and date): 
November 12, 2004
SLAC-I-730-0A11R-002
Electrical Work Plan, Page 1 of 1

