Electrical Work Plan
(Reference ES&H Bulletin 68A. Attach additional pages as needed)
Job Name:
   Intermediate Power Supply, Troubleshoot, Test and Repair

Location:
   B118 Test Stand

Effective Dates Of Plan -  Start:
   02/28/2005

End:
   02/27/2006

Work To Be Performed By:
  
Fernando Rafael, Greg Johnson and Critt Taylor

Person In Charge:   Fernando Rafael

Phone:
   x4607

Description Of Work:
Troubleshoot, test and repair SPEAR3 Intermediate Power Supplies.
The Intermediate Power Supplies must be test using the following test equipment:
· Intermediate power supply to be tested
· Test stand located in B118

· One BitBus Controller and respective DC-DC sensor (two)

· Local Control Board

· Rated Load

· Test equipment is listed in Unipolar Switch Mode Intermediate DC Power Supply Test Procedure
Associated Hazards (e.g. voltage, current, etc.):
3 phase 480 VAC Input
Combination of up to 150 Vdc and 100 A Output,  max: 22.5 kW
Hazard Mitigation (e.g. specific PPE, barriers, etc):
· Use: V:\SSRL-ED&M\Group\Power Supplies\SPEAR3\Intermediate\ Test Procedure _SLAC

Document #  Unipolar Switch Mode Intermediate DC Power Supplies Test Procedure
IE POWER Model:   9250J0, J1, J2, J3, J4, H1, H2

9240E0, F0

· Two person rule.
· Lock Out the system using appropriate ELP Procedure.??
· Use PPE:
-  Hazard Risk Category 0 clothing, non-melting, flammable materials, (i.e. untreated cotton, wool, rayon, or silk, or blends of these materials) Shirt (long sleeve), pants (long), closed toe work shoes.

-  Electrical safety glasses/goggles w/UV Protection
-  Gloves
Inspection Required After Work?  -  Yes
 
 
No 
X

(Required for New Installations.)
Originator:
Fernando Rafael

Date:
   01/28/2005

Approvals As Required By Bulletin 68a (Sign, print name and title, and date):

Participants (All workers to read, sign, print name and date): 
November 12, 2004
SLAC-I-730-0A11R-002
Electrical Work Plan, Page 1 of 2

