{"text_format":"2","workbook":"xls","n_sheets":2,"sheets":["Power Supply List","Lookup Tables"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":1,"defined_names":7,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Power Supply List","index":0,"n_rows":320,"n_cols":71,"rows_kept":320,"cut":false,"hidden":false,"merged":[[3,16,3,22],[2,63,2,64],[0,68,0,70],[0,55,0,59],[3,55,3,58],[2,55,2,59],[0,45,0,46],[0,48,0,53],[2,34,2,42],[0,61,0,64],[280,1,280,2],[0,0,0,14],[3,28,3,32],[0,24,0,42],[3,1,3,9],[3,11,3,14],[1,10,1,13],[0,16,0,21],[3,34,3,42],[2,16,2,22]],"flags":["formulas_cached_only"]}
["Magnet Data",{"$nulls":15},"Cable Data",{"$nulls":7},"Power Supply Data",{"$nulls":19},"Contlr","Xductor",null,null,"Daughter-Board EEPROM",{"$nulls":6},"AC Input Data",{"$nulls":5},"PPS/MPS",{"$nulls":4},"Cooling",null,"Drawing"]
[]
[{"$nulls":16},"Individual or String",{"$nulls":17},"DC Rating",{"$nulls":20},"Standardizing AC Input",{"$nulls":5},"PPS",null,"MPS",null,null,"Air/"]
[null,"Magnet",{"$nulls":9},"Standardizing",{"$nulls":4},"Based on Standardizing I +10%",{"$nulls":11},"Standardizing Needs",{"$nulls":5},"(Each)",{"$nulls":20},"(ea PS)",null,null,null,"Total",null,"Data",null,"PS or BB","Elevation",null,"Water",null,"Number",null,"Suffix"]
["Magnet  Data Reference","Name","Qty","Regions","String (s) or Individually (I) Powered","Single Magnet Inductance (H)","40C Single Magnet or Load Resistance (ohms)","Maximum Ramp di/dt (A/sec)","Max Ripple I % Imax","Stability dI/I In %",null,"Single Peak Volts (40C)","Total Peak Volts (40C)","Peak Amps","di/dt Volts",null,"NEC Type or Other Data","1/C, 2/C or 3/C","1/C R (75C) (Ohm/kft)","Round Trip Length(ft)",null,"Voltage    Drop (V)","B118 Cable Loss (kW) ",null,"Tag Number","LGPS Number","Qty",null,"Resistive Volts (Includes Ramp di/dt)","Inductive Volts (Corrector or QMS)","Total Volts","Total Amps","kW Dissipated",null,"Volts","Volt Margin ","Amps","Amp Margin","kW","kW Margin","Power Supply Loss in B118",null,"Freestanding (F) or Rack-Mounted (R)",null,"Bitbus Controller Quantity","Amps","Quantity",null,"BitBus Address","Regulating Transductor Amps/Volt","Auxiliary Transductor Amps/Volt","Power Supply Output Volts/Volt ","Ground Current Amps/Volt","Magnet/Power Supply Name",null,"Volts","Amps","# of Phases","kVA","Expected Running kVA",null,"MCC Feeder     4PB118-MCC-XX  or 2PB118-DP-03",null,"Power Supply or BitBus","Elevation of MPS Interface (BitBus or Power Supply)"]
[]
[" S30731 M313 Rev B 99-07-29","01G-BDM1,BDM2, 02G-BD1,BD2, 03G-BD1,BD2, 04G-BD1,BD2, 05G-BD1,BD2, 05G-BD2, 06G-BD1,BD2, 07G-BD1,BD2, 08G-BD1,BD2, 09G-BDM1,BDM2, 10G-BDM1,BDM2, 11G-BD1,BD2, 12G-BD1,BD2, 13G-BD1,BD2, 14G-BD1,BD2, 15G-BD1,BD2, 16G-BD1,BD2, 17G-BD1,BD2, 18G-BDM1,BDM2",36,"Ring","S",0.067,0.041037187681580475,11.473333333333333,0.005,0.005,null,28.25,1017,688.4,27.673679999999997,null,"1\"SQ AL","1/C",0.017,2560,43.52,29.959168,2.416862256,null,"MS1-BD-PS",2,1,null,1074.6328480000002,"NA",1074.6328480000002,688.4,739.7772525632,null,1200,0.11666045034201279,775,0.12579895409645558,930,0.2571351670759152,16.439494501404443,null,"R",null,1,1000,2,null,2,{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-02A and MCC-02B",null,"Power Supply","B118-PS7",null,"Water 26.2 GPM @ 141 psig diff"]
["Not applicable","Dipole Bulk","NA","NA","NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA",null,"MS1-BD-PS",1,1,null,1343.2910600000002,"NA",1343.2910600000002,688,813.75497781952,null,1500,0.11666045034201279,775,0.12645348837209303,1023.0000000000001,0.2571351670759153,18.083443951544883,null,"F",null,1,1000,1,null,1,{"$nulls":6},480,1346.811304605257,3,1063.7319971496993,1063.7319971496993,null,"MCC-02A and MCC-02B",null,"Power Supply","B118-PS7",null,"Water 9.6 GPM @ 147psig diff"]
[]
[" S30732 M314 Rev B 99-08-02","02G-QD1,QD2 03G-QD1,QD2 04G-QD1,QD2",6,"Ring","S",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,270.96,88.24,1.023584,null,"#2","2/C",0.201,1000,null,17.73624,0.46951374527999995,null,"MS1-QD-PS",3,1,null,289.719824,"NA",289.719824,88.24,25.56487726976,null,700,1.41612738243276,100,0.13327289211242074,70,1.7381316664015867,4.511448929957648,null,"F",null,1,150,2,null,3,15,15,70,0.01,"QD1,QD2",null,480,42.31134265994634,3,33.418140221908494,33.418140221908494,null,"MCC-03",null,"Power Supply","B118-PS6",null,"Air",null,null,null,56]
[" S30732 M314 Rev B 99-08-02","05G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"05G-QD1-PS",4,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,4,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3135",null,"Air",null,null,null,"01"]
[" S30732 M314 Rev B 99-08-02","05G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"05G-QD2-PS",5,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,5,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3133",null,"Air",null,null,null,"02"]
[" S30732 M314 Rev B 99-08-02","06G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"06G-QD1-PS",6,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,6,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3131",null,"Air",null,null,null,"03"]
[" S30732 M314 Rev B 99-08-02","06G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"06G-QD2-PS",7,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,7,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3129",null,"Air",null,null,null,"04"]
[" S30732 M314 Rev B 99-08-02","07G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"07G-QD1-PS",8,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,8,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3235",null,"Air",null,null,null,"05"]
[" S30732 M314 Rev B 99-08-02","07G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"07G-QD2-PS",9,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,9,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3233",null,"Air",null,null,null,"06"]
[" S30732 M314 Rev B 99-08-02","08G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"08G-QD1-PS",10,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,10,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3231",null,"Air",null,null,null,"07"]
[" S30732 M314 Rev B 99-08-02","08G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"08G-QD2-PS",11,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,11,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3229",null,"Air",null,null,null,"08"]
[" S30732 M314 Rev B 99-08-02","11G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"11G-QD1-PS",12,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,12,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3335",null,"Air",null,null,null,"09"]
[" S30732 M314 Rev B 99-08-02","11G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"11G-QD2-PS",13,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,13,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3333",null,"Air",null,null,null,"10"]
[" S30732 M314 Rev B 99-08-02","12G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"12G-QD1-PS",14,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,14,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3331",null,"Air",null,null,null,"11"]
[" S30732 M314 Rev B 99-08-02","12G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"12G-QD2-PS",15,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,15,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3329",null,"Air",null,null,null,"12"]
[" S30732 M314 Rev B 99-08-02","13G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"13G-QD1-PS",16,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,16,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3435",null,"Air",null,null,null,"13"]
[" S30732 M314 Rev B 99-08-02","13G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"13G-QD2-PS",17,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,17,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3433",null,"Air",null,null,null,"14"]
[" S30732 M314 Rev B 99-08-02","14G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"14G-QD1-PS",18,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,18,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3431",null,"Air",null,null,null,"15"]
[" S30732 M314 Rev B 99-08-02","14G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"14G-QD2-PS",19,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,19,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3429",null,"Air",null,null,null,"16"]
[" S30732 M314 Rev B 99-08-02","15G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"15G-QD1-PS",20,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,20,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3535",null,"Air",null,null,null,"17"]
[" S30732 M314 Rev B 99-08-02","15G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"15G-QD2-PS",21,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,21,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3533",null,"Air",null,null,null,"18"]
[" S30732 M314 Rev B 99-08-02","16G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"16G-QD1-PS",22,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,22,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3531",null,"Air",null,null,null,"19"]
[" S30732 M314 Rev B 99-08-02","16G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"16G-QD2-PS",23,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,23,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3529",null,"Air",null,null,null,"20"]
[" S30732 M314 Rev B 99-08-02","17G-QD1",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"17G-QD1-PS",24,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,24,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3631",null,"Air",null,null,null,"21"]
[" S30732 M314 Rev B 99-08-02","17G-QD2",1,"Ring","I",0.116,0.5117860380779692,1.4706666666666666,0.01,0.01,null,45.16,45.16,88.24,0.17059733333333332,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"17G-QD2-PS",25,1,null,59.51958933333333,"NA",59.51958933333333,88.24,5.252008562773333,null,100,0.6801191191014492,100,0.13327289211242074,10,0.9040334531974719,0.9268250404894118,null,"R",null,1,150,2,null,25,{"$nulls":6},480,8.692376325832482,3,6.865370670291938,6.865370670291938,null,"MCC-03",null,"BitBus","B118-3629",null,"Air",null,null,null,"22"]
[]
[" S30732 M314 Rev B 99-08-02","02G-QF1,QF2  03G-QF1,QF2  04G-QF1,QF2",6,"Ring","S",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,404.82,88.24,2.329536,null,"#2","2/C",0.201,1000,null,17.73624,0.46951374527999995,null,"MS1-QF-PS",26,1,null,424.885776,"NA",424.885776,88.24,37.49192087424,null,700,0.6475016099385732,100,0.13327289211242074,70,0.867068914254956,6.616221330748239,null,"F",null,1,150,2,null,26,15,15,70,0.01,"QF1,QF2",null,480,62.05128600269068,3,49.00904689443137,49.00904689443137,null,"MCC-03",null,"Power Supply","B118-PS5",null,"Air",null,null,null,57]
[" S30732 M314 Rev B 99-08-02","05G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"05G-QF1-PS",27,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,27,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0135",null,"Air",null,null,null,"23"]
[" S30732 M314 Rev B 99-08-02","05G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"05G-QF2-PS",28,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,28,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0133",null,"Air",null,null,null,"24"]
[" S30732 M314 Rev B 99-08-02","06G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"06G-QF1-PS",29,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,29,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0131",null,"Air",null,null,null,"25"]
[" S30732 M314 Rev B 99-08-02","06G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"06G-QF2-PS",30,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,30,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0129",null,"Air",null,null,null,"26"]
[" S30732 M314 Rev B 99-08-02","07G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"07G-QF1-PS",31,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,31,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0235",null,"Air",null,null,null,"27"]
[" S30732 M314 Rev B 99-08-02","07G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"07G-QF2-PS",32,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,32,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0233",null,"Air",null,null,null,"28"]
[" S30732 M314 Rev B 99-08-02","08G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"08G-QF1-PS",33,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,33,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0231",null,"Air",null,null,null,"29"]
[" S30732 M314 Rev B 99-08-02","08G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"08G-QF2-PS",34,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,34,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0229",null,"Air",null,null,null,"30"]
[" S30732 M314 Rev B 99-08-02","11G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"11G-QF1-PS",35,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,35,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0335",null,"Air",null,null,null,"31"]
[" S30732 M314 Rev B 99-08-02","11G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"11G-QF2-PS",36,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,36,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0333",null,"Air",null,null,null,"32"]
[" S30732 M314 Rev B 99-08-02","12G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"12G-QF1-PS",37,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,37,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0331",null,"Air",null,null,null,"33"]
[" S30732 M314 Rev B 99-08-02","12G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"12G-QF2-PS",38,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,38,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0329",null,"Air",null,null,null,"34"]
[" S30732 M314 Rev B 99-08-02","13G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"13G-QF1-PS",39,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,39,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0435",null,"Air",null,null,null,"35"]
[" S30732 M314 Rev B 99-08-02","13G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"13G-QF2-PS",40,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,40,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0433",null,"Air",null,null,null,"36"]
[" S30732 M314 Rev B 99-08-02","14G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"14G-QF1-PS",41,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,41,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0431",null,"Air",null,null,null,"37"]
[" S30732 M314 Rev B 99-08-02","14G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"14G-QF2-PS",42,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,42,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0429",null,"Air",null,null,null,"38"]
[" S30732 M314 Rev B 99-08-02","15G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"15G-QF1-PS",43,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,43,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0535",null,"Air",null,null,null,"39"]
[" S30732 M314 Rev B 99-08-02","15G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"15G-QF2-PS",44,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,44,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0533",null,"Air",null,null,null,"40"]
[" S30732 M314 Rev B 99-08-02","16G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"16G-QF1-PS",45,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,45,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0531",null,"Air",null,null,null,"41"]
[" S30732 M314 Rev B 99-08-02","16G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"16G-QF2-PS",46,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,46,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0529",null,"Air",null,null,null,"42"]
[" S30732 M314 Rev B 99-08-02","17G-QF1",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"17G-QF1-PS",47,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,47,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0631",null,"Air",null,null,null,"43"]
[" S30732 M314 Rev B 99-08-02","17G-QF2",1,"Ring","I",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,67.47,88.24,0.388256,null,"#2","2/C",0.201,800,null,14.188991999999999,0.46951374527999995,null,"17G-QF2-PS",48,1,null,82.047248,"NA",82.047248,88.24,7.239849163519999,null,100,0.21880992278985403,100,0.13327289211242074,10,0.38124424613537417,1.2776204406211757,null,"R",null,1,150,2,null,48,{"$nulls":6},480,11.982366882956537,3,9.463855115712416,9.463855115712416,null,"MCC-03",null,"BitBus","B118-0629",null,"Air",null,null,null,"44"]
[]
[" S30732 M314 Rev B 99-08-02","02G-QFC, 03G-QFC, 04G-QFC, 05G-QFC, 06G-QFC, 07G-QFC, 08G-QFC",7,"Ring","S",0.388,0.9775611967361741,1.4706666666666666,0.01,0.01,null,86.26,603.82,88.24,3.9943306666666665,null,"#2","2/C",0.201,940,null,16.6720656,0.46951374527999995,null,"MS1-QFC-PS",49,1,null,624.4863962666667,"NA",624.4863962666667,88.24,55.10467960657066,null,700,0.12092113484740773,100,0.13327289211242074,70,0.2703095363184586,9.724355224688942,null,"F",null,1,150,2,null,49,15,15,70,0.01,"QFC1",null,480,91.20141498813685,3,72.03226092362178,72.03226092362178,null,"MCC-03",null,"Power Supply","B118-PS3",null,"Air",null,null,null,60]
[" S30732 M314 Rev B 99-08-02","11G-QFC, 12G-QFC, 13G-QFC, 14G-QFC, 15G-QFC, 16G-QFC, 17G-QFC",7,"Ring","S",0.388,0.9775611967361741,1.4706666666666666,0.01,0.01,null,86.26,603.82,88.24,3.9943306666666665,null,"#2","2/C",0.201,1200,null,21.283488,0.46951374527999995,null,"MS2-QFC-PS",50,1,null,629.0978186666667,"NA",629.0978186666667,88.24,55.51159151914667,null,700,0.11270454169370031,100,0.13327289211242074,70,0.2609978940318454,9.796163209261174,null,"F",null,1,150,2,null,50,15,15,70,0.01,"QFC2",null,480,91.87487761358754,3,72.56417192045316,72.56417192045316,null,"MCC-03",null,"Power Supply","B118-PS4",null,"Air",null,null,null,61]
[]
[" S30732 M314 Rev B 99-08-02","01G-QDX, 09G-QDX, 10G-QDX, 18G-QDX",4,"Pits","S",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,269.88,88.24,1.553024,null,"#2","2/C",0.201,1120,null,19.864588799999996,0.46951374527999995,null,"MS1-QDX-PS",51,2,null,291.29761279999997,"NA",291.29761279999997,88.24,25.704101353471998,null,150,0.02987455721435982,100,0.13327289211242074,15,0.16712891796731616,9.072035771813646,null,"R",null,1,150,2,null,51,{"$nulls":6},480,21.270883264110314,3,16.800066244099344,33.60013248819869,null,"MCC-04",null,"BitBus","B118-0831",null,"Air",null,null,null,"45"]
[" S30732 M314 Rev B 99-08-02","01G-QDY, 09G-QDY, 10G-QDY, 18G-QDY",4,"Pits","S",0.264,0.7647325475974613,1.1030000000000002,0.01,0.01,null,50.61,202.44,66.18,1.1647680000000002,null,"#2","2/C",0.201,1120,null,14.898441600000002,0.2641014817200001,null,"MS1-QDY-PS",52,2,null,218.50320960000002,"NA",218.50320960000002,66.18,14.460542411328003,null,125,0.14414795305597186,80,0.2088244182532486,10,0.38307398374853036,5.103720851056941,null,"R",null,1,150,2,null,52,{"$nulls":6},480,11.966514811673292,3,9.451334909364707,18.902669818729414,null,"MCC-04",null,"BitBus","B118-0829",null,"Air",null,null,null,"46"]
[" S30732 M314 Rev B 99-08-02","01G-QDZ, 09G-QDZ, 10G-QDZ, 18G-QDZ",4,"Pits","S",0.264,0.7647325475974613,1.1030000000000002,0.01,0.01,null,50.61,202.44,66.18,1.1647680000000002,null,"#2","2/C",0.201,1120,null,14.898441600000002,0.2641014817200001,null,"MS1-QDZ-PS",53,2,null,218.50320960000002,"NA",218.50320960000002,66.18,14.460542411328003,null,125,0.14414795305597186,80,0.2088244182532486,10,0.38307398374853036,5.103720851056941,null,"R",null,1,150,2,null,53,{"$nulls":6},480,11.966514811673292,3,9.451334909364707,18.902669818729414,null,"MCC-04",null,"BitBus","B118-0931",null,"Air",null,null,null,"47"]
[" S30732 M314 Rev B 99-08-02","01G-QFX, 09G-QFX, 10G-QFX, 18G-QFX",4,"Pits","S",0.466,1.1107663248785753,1.2353333333333334,0.01,0.01,null,82.33,329.32,74.12,2.3026613333333334,null,"#2","2/C",0.201,1120,null,16.685894400000002,0.33127459632,null,"MS1-QFX-PS",54,2,null,348.3085557333333,"NA",348.3085557333333,74.12,25.81663015095467,null,200,0.14840704718790168,75,0.011872638963842356,15,0.16204166944269582,9.111751817984,null,"R",null,1,150,2,null,54,{"$nulls":6},480,21.36400408098654,3,16.87361447774815,33.7472289554963,null,"MCC-04",null,"BitBus","B118-0929",null,"Air",null,null,null,"48"]
[" S30732 M314 Rev B 99-08-02","01G-QFY, 09G-QFY, 10G-QFY, 18G-QFY",4,"Pits","S",0.388,0.9776367482623148,1.1030000000000002,0.01,0.01,null,64.7,258.8,66.18,1.7118560000000003,null,"#2","2/C",0.201,1120,null,14.898441600000002,0.2641014817200001,null,"MS1-QFY-PS",55,2,null,275.41029760000004,"NA",275.41029760000004,66.18,18.226653495168005,null,150,0.08928388885339908,100,0.5110305228165607,15,0.6459412040698079,6.432936527706353,null,"R",null,1,150,2,null,55,{"$nulls":6},480,15.083080068027295,3,11.912845421678435,23.82569084335687,null,"MCC-04",null,"BitBus","B118-1031",null,"Air",null,null,null,"49"]
[" S30732 M314 Rev B 99-08-02","01G-QFZ, 09G-QFZ, 10G-QFZ, 18G-QFZ",4,"Pits","S",0.264,0.7646192203082502,1.4706666666666666,0.01,0.01,null,67.47,269.88,88.24,1.553024,null,"#2","2/C",0.201,1120,null,19.864588799999996,0.46951374527999995,null,"MS1-QFZ-PS",56,2,null,291.29761279999997,"NA",291.29761279999997,88.24,25.704101353471998,null,150,0.02987455721435982,100,0.13327289211242074,15,0.16712891796731616,9.072035771813646,null,"R",null,1,150,2,null,56,{"$nulls":6},480,21.270883264110314,3,16.800066244099344,33.60013248819869,null,"MCC-04",null,"BitBus","B118-1029",null,"Air",null,null,null,"50"]
[]
[" S30735 M315 Rev B 99-08-04","02G-SD1,SD2, 03G-SD1,SD2, 04G-SD1,SD2, 05G-SD1,SD2, 06G-SD1,SD2, 07G-SD1,SD2, 08G-SD1,SD2, 11G-SD1,SD2, 12G-SD1,SD2, 13G-SD1,SD2, 14G-SD1,SD2, 15G-SD1,SD2, 16G-SD1,SD2 17G-SD1,SD2 ",28,"Ring","S",0.02,0.09122311958742824,3.4256666666666664,0.05,0.05,null,18.75,525,205.54,1.9183733333333335,null,"#4/0","1/C",0.0626,2360,null,30.36565744,0.793392868248,null,"MS1-SD-PS",57,1,null,557.2840307733333,"NA",557.2840307733333,205.54,114.54415968515092,null,600,0.07665026605444004,225,0.09467743504913889,135,0.17858475168944737,4.042735047711207,null,"F",null,1,600,2,null,57,30,30,60,0.01,"SD",null,480,189.5771741437948,3,149.73092769300774,149.73092769300774,null,"MCC-04",null,"Power Supply","B118-PS1",null,"Water 2.5gpm @ 60psig diff",null,null,null,62]
[" S30735 M315 Rev B 99-08-04","02G-SF1,SF2, 03G-SF1,SF2, 04G-SF1,SF2, 05G-SF1,SF2, 06G-SF1,SF2, 07G-SF1,SF2, 08G-SF1,SF2, 11G-SF1,SF2, 12G-SF1,SF2, 13G-SF1,SF2, 14G-SF1,SF2, 15G-SF1,SF2, 16G-SF1,SF2 17G-SF1,SF2 ",28,"Ring","S",0.0168,0.08191935778142674,2.7405,0.05,0.05,null,13.47,377.16,164.43,1.2891312,null,"#4/0","1/C",0.0626,2360,null,24.29223048,0.507759083622,null,"MS1-SF-PS",58,1,null,402.74136168,"NA",402.74136168,164.43,66.2227621010424,null,600,0.48978986786247386,225,0.3683634373289545,135,1.0385739844861437,2.33727395650738,null,"F",null,1,600,2,null,58,30,30,60,0.01,"SF",null,480,109.60248115330062,3,86.56570209286589,86.56570209286589,null,"MCC-04",null,"Power Supply","B118-PS2",null,"Water 2.5gpm @ 60psig diff",null,null,null,63]
[]
[" S30735 M315 Rev B 99-08-04","01G-SDM1,SDM2, 09G-SDM1,SDM2, 10G-SDM1,SDM2, 18G-SDM1,SDM2",8,"Pits","S",0.0168,0.08190074602659747,2.055333333333333,0.05,0.05,null,10.1,80.8,123.32,0.27623679999999995,null,"#4/0","1/C",0.0626,1150,null,8.8778068,0.285602904672,null,"MS1-SDM-PS",59,1,null,89.9540436,"NA",89.9540436,123.32,11.093132656752001,null,100,0.11167876393274213,150,0.21634771326629912,15,0.35218792239629676,1.9576116453091768,null,"R",null,1,150,2,null,59,{"$nulls":6},480,18.359772748343072,3,14.500827002290197,14.500827002290197,null,"MCC-04",null,"BitBus","B118-0731",null,"Air",null,null,null,64]
[" S30735 M315 Rev B 99-08-04","01G-SFM1,SFM2,  09G-SFM1,SFM2, 10G-SFM1,SFM2, 18G-SFM1,SFM2",8,"Pits","S",0.0168,0.08190074602659747,2.055333333333333,0.05,0.05,null,10.1,80.8,123.32,0.27623679999999995,null,"#4/0","1/C",0.0626,1150,null,8.8778068,0.285602904672,null,"MS1-SFM-PS",60,1,null,89.9540436,"NA",89.9540436,123.32,11.093132656752001,null,100,0.11167876393274213,150,0.21634771326629912,15,0.35218792239629676,1.9576116453091768,null,"R",null,1,150,2,null,60,{"$nulls":6},480,18.359772748343072,3,14.500827002290197,14.500827002290197,null,"MCC-04",null,"BitBus","B118-0729",null,"Air",null,null,null,65]
[]
["DellOrco 7/16/01 SS","B9V Septum",1,"Ring","I",0.0546,0.10043272854527834,4.953066666666667,0.05,0.05,null,29.847,29.847,297.184,0.27043744000000003,null,"#373","1/C",0.0359,680,null,7.254855808000001,0.9511884125491201,null,"BTS-B9V-PS",61,1,null,37.372293248,"NA",37.372293248,297.184,11.106447596613632,null,50,0.33788953405142674,300,0.00947561106923648,15,0.3505668549297001,1.959961340578877,null,"R",null,1,600,2,null,61,{"$nulls":6},480,18.381809739838758,3,14.51823215243612,14.51823215243612,null,"MCC-04",null,"BitBus","B118-1231",null,"Air",null,null,null,51]
[]
[]
["J Tanabe email of 00-08-02","01G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"01G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","01G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"01G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","01G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"01G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","01G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"01G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","01G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"01G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","01G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"01G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","02G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"02G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","02G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"02G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR01-PS","NA",1,null,60,"NA",60,58.14195436638954,3.4885172619833726,null,80,0.3333333333333333,125,1.1499105312541658,10,1.8665473750055541,0.6156206932911834,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.773696767224964,3,4.560153283638395,4.560153283638395,null,"MCC-01",null,"Power Supply","B118-3811",null,"Air"]
[]
["J Tanabe email of 00-08-02","02G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"02G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","02G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"02G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","02G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"02G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","02G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"02G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","03G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"03G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","03G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"03G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","03G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"03G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","03G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"03G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR02-PS","NA",1,null,60,"NA",60,58.70768646353228,3.522461187811937,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955389,0.6216107978491654,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.82987591730659,3,4.6045244285123355,4.6045244285123355,null,"MCC-01",null,"Power Supply","B118-3806",null,"Air"]
[{"$nulls":66},"Air"]
["J Tanabe email of 00-08-02","03G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"03G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","03G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"03G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","04G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"04G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","04G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"04G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","04G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"04G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","04G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"04G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","04G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"04G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","04G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"04G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR03-PS","NA",1,null,60,"NA",60,58.70768646353228,3.5224611878119374,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955384,0.6216107978491658,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.829875917306591,3,4.604524428512336,4.604524428512336,null,"MCC-01",null,"Power Supply","B118-3801",null,"Air"]
[]
["J Tanabe email of 00-08-02","05G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"05G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","05G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"05G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","05G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"05G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","05G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"05G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","05G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"05G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","05G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"05G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","06G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"06G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","06G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"06G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR04-PS","NA",1,null,60,"NA",60,58.70768646353228,3.522461187811937,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955389,0.6216107978491654,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.82987591730659,3,4.6045244285123355,4.6045244285123355,null,"MCC-01",null,"Power Supply","B118-3911",null,"Air"]
[]
["J Tanabe email of 00-08-02","06G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"06G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","06G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"06G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","06G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"06G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","06G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"06G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","07G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"07G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","07G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"07G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","07G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"07G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","07G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"07G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR05-PS","NA",1,null,60,"NA",60,58.70768646353228,3.522461187811937,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955389,0.6216107978491654,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.82987591730659,3,4.6045244285123355,4.6045244285123355,null,"MCC-01",null,"Power Supply","B118-3906",null,"Air"]
[]
["J Tanabe email of 00-08-02","07G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"07G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","07G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"07G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","08G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"08G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","08G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"08G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","08G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"08G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","08G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"08G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","08G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"08G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","08G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"08G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR06-PS","NA",1,null,60,"NA",60,58.70768646353228,3.5224611878119374,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955384,0.6216107978491658,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.829875917306591,3,4.604524428512336,4.604524428512336,null,"MCC-01",null,"Power Supply","B118-3901",null,"Air"]
[]
["J Tanabe email of 00-08-02","09G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"09G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","09G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"09G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","09G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"09G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","09G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"09G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","09G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"09G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","09G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"09G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","10G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"10G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","10G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"10G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR07-PS","NA",1,null,60,"NA",60,58.70768646353228,3.522461187811937,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955389,0.6216107978491654,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.82987591730659,3,4.6045244285123355,4.6045244285123355,null,"MCC-01",null,"Power Supply","B118-4011",null,"Air"]
[]
["J Tanabe email of 00-08-02","10G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"10G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","10G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"10G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","10G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"10G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","10G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"10G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","11G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"11G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","11G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"11G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","11G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"11G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","11G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"11G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR08-PS","NA",1,null,60,"NA",60,58.70768646353228,3.522461187811937,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955389,0.6216107978491654,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.82987591730659,3,4.6045244285123355,4.6045244285123355,null,"MCC-01",null,"Power Supply","B118-4006",null,"Air"]
[]
["J Tanabe email of 00-08-02","11G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"11G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","11G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"11G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","12G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"12G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","12G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"12G-COR1V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","12G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"12G-COR2V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","12G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"12G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","12G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"12G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","12G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"12G-COR4V-PS","NA",1,null,23.781197499999998,17.83167990177567,41.61287740177566,22.13,0.4604464884506477,null,50,0.20155113325247848,30,0.3556258472661546,1.5,2.257707546097999,0.08125526266776134,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR09-PS","NA",1,null,60,"NA",60,58.70768646353228,3.5224611878119374,null,80,0.3333333333333333,125,1.129193084071654,10,1.8389241120955384,0.6216107978491658,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.829875917306591,3,4.604524428512336,4.604524428512336,null,"MCC-01",null,"Power Supply","B118-4001",null,"Air"]
[]
["J Tanabe email of 00-08-02","13G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"13G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","13G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"13G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","13G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"13G-COR2V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","13G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"13G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","13G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"13G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","13G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"13G-COR4V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","14G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"14G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","14G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"14G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR10-PS","NA",1,null,60,"NA",60,56.44475807496132,3.3866854844976793,null,80,0.3333333333333333,125,1.2145546240803098,10,1.9527394987737465,0.5976503796172374,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.605159316980086,3,4.427039849016574,4.427039849016574,null,"MCC-01",null,"Power Supply","B118-4111",null,"Air"]
[]
["J Tanabe email of 00-08-02","14G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"14G-COR2V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","14G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"14G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","14G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"14G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","14G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"14G-COR4V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","15G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"15G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","15G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"15G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","15G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"15G-COR2V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","15G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"15G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR11-PS","NA",1,null,60,"NA",60,56.44475807496132,3.3866854844976793,null,80,0.3333333333333333,125,1.2145546240803098,10,1.9527394987737465,0.5976503796172374,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.605159316980086,3,4.427039849016574,4.427039849016574,null,"MCC-01",null,"Power Supply","B118-4106",null,"Air"]
[]
["J Tanabe email of 00-08-02","15G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"15G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","15G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"15G-COR4V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","16G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"16G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","16G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"16G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","16G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"16G-COR2V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","16G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"16G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","16G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"16G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","16G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"16G-COR4V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR12-PS","NA",1,null,60,"NA",60,56.44475807496133,3.3866854844976797,null,80,0.3333333333333333,125,1.2145546240803096,10,1.952739498773746,0.5976503796172379,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.605159316980088,3,4.427039849016575,4.427039849016575,null,"MCC-01",null,"Power Supply","B118-4101",null,"Air"]
[]
["J Tanabe email of 00-08-02","17G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"17G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","17G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"17G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","17G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"17G-COR2V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","17G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"17G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","17G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"17G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","17G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"17G-COR4V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","18G-COR1H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"18G-COR1H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","18G-COR1V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"18G-COR1V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA",0,"NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR13-PS","NA",1,null,60,"NA",60,56.44475807496132,3.3866854844976793,null,80,0.3333333333333333,125,1.2145546240803098,10,1.9527394987737465,0.5976503796172374,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,5.605159316980086,3,4.427039849016574,4.427039849016574,null,"MCC-01",null,"Power Supply","B118-4211",null,"Air"]
[{"$nulls":66},"Air"]
["J Tanabe email of 00-08-02","18G-COR2V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"18G-COR2V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","18G-COR3H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"18G-COR3H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","18G-COR4H",1,"Ring","I",0.04510000000000001,0.512,0,0.01,0.05,null,7.68,7.68,22.13,0,null,"#6","2/C",0.51,825,null,9.311197499999999,0.0749297457,null,"18G-COR4H-PS","NA",1,null,16.9911975,17.00229944122796,33.99349694122796,22.13,0.37613804365468734,null,50,0.47086956327105756,30,0.3556258472661546,1.5,2.9878975958546525,0.06637730182141544,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","18G-COR4V",1,"Ring","I",0.0473,0.902,0,0.01,0.05,null,14.47,14.47,20.85,0,null,"#6","2/C",0.51,825,null,8.7726375,0.06651254250000002,null,"18G-COR4V-PS","NA",1,null,23.2426375,17.83167990177567,41.07431740177567,20.85,0.4281997589135114,null,50,0.217305683035854,30,0.43884892086330923,1.5,2.5030379367938242,0.07556466333767847,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","SPACE",0,"NA","NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA",null,"SPACE","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA","NA","NA",null,"NA",null,"NA","NA","NA",null,"NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","SPACE",0,"NA","NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA",null,"SPACE","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA","NA","NA",null,"NA",null,"NA","NA","NA",null,"NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","QMS (See Below)",1,"Ring","I",0.004,0.17454858125537398,0,0.01,0.05,null,2.870853531617383,2.870853531617383,16.4473037303991,0,null,"#6","2/C",0.51,820,null,6.878262420052904,0.04138861140000002,null,"QMS (See Below)","NA",1,null,9.749115951670287,4.133658285662545,10.589258362214922,16.4473037303991,0.08708237428150868,null,50,3.7217659905638243,30,0.8240071741699416,1.5,16.22507008308011,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["J Tanabe email of 00-08-02","SPACE",0,"NA","NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA",null,"SPACE","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA","NA","NA",null,"NA",null,"NA","NA","NA",null,"NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
[null,"Corrector Bulk","NA","NA","NA","NA","NA","NA",0.01,0.1,null,60,60,"NA",0,null,"NA","NA","NA","NA",null,0,0,null,"118-MCOR14-PS","NA",1,null,60,"NA",60,29.750139989787833,1.7850083993872699,null,80,0.3333333333333333,125,3.201660901189307,10,4.602214534919077,0.31500148224481217,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,2.9542915946909285,3,2.333344312924536,2.333344312924536,null,"MCC-01",null,"Power Supply","B118-4206",null,"Air"]
[]
["No reference - assumed data","ID4T-H",1,"Ring","I",0,1.2280701754385965,0,0.01,0.05,null,35,35,28.5,0,null,"#6","2/C",0.51,800,null,11.628,0.12427425,null,"13S-ID4TH-PS","NA",1,null,46.628,"NA",46.628,28.5,1.328898,null,50,0.07231706270910182,30,0.05263157894736842,1.5,0.1287548028516862,0.2345114117647058,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["No reference - assumed data","ID4T-O",1,"Ring","I",0,1.2280701754385965,0,0.01,0.05,null,35,35,28.5,0,null,"#6","2/C",0.51,800,null,11.628,0.12427425,null,"13S-ID4TO-PS","NA",1,null,46.628,"NA",46.628,28.5,1.328898,null,50,0.07231706270910182,30,0.05263157894736842,1.5,0.1287548028516862,0.2345114117647058,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["No reference - assumed data","ID7T-H",1,"Ring","I",0,1.2280701754385965,0,0.01,0.05,null,35,35,28.5,0,null,"#6","2/C",0.51,800,null,11.628,0.12427425,null,"05S-ID7TH-PS","NA",1,null,46.628,"NA",46.628,28.5,1.328898,null,50,0.07231706270910182,30,0.05263157894736842,1.5,0.1287548028516862,0.2345114117647058,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["No reference - assumed data","ID7T-O",1,"Ring","I",0,1.2280701754385965,0,0.01,0.05,null,35,35,28.5,0,null,"#6","2/C",0.51,800,null,11.628,0.12427425,null,"05S-ID7TO-PS","NA",1,null,46.628,"NA",46.628,28.5,1.328898,null,50,0.07231706270910182,30,0.05263157894736842,1.5,0.1287548028516862,0.2345114117647058,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["No reference - assumed data","ID5T-H",1,"Ring","I",0,1.2280701754385965,0,0.01,0.05,null,35,35,28.5,0,null,"#6","2/C",0.51,800,null,11.628,0.12427425,null,"12S-ID5TH-PS","NA",1,null,46.628,"NA",46.628,28.5,1.328898,null,50,0.07231706270910182,30,0.05263157894736842,1.5,0.1287548028516862,0.2345114117647058,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["No reference - assumed data","ID6T-H",1,"Ring","I",0,1.2280701754385965,0,0.01,0.05,null,35,35,28.5,0,null,"#6","2/C",0.51,800,null,11.628,0.12427425,null,"11S-ID6TH-PS","NA",1,null,46.628,"NA",46.628,28.5,1.328898,null,50,0.07231706270910182,30,0.05263157894736842,1.5,0.1287548028516862,0.2345114117647058,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","BTS-C8H",1,"BTS","I",0.0032,0.026,0,0,0.05,null,0.45,0.45,16.93,0,null,"#6","2/C",0.51,825,null,7.1232975,0.0438536097,null,"BTS-C8H-PS","NA",1,null,7.5732975,1.2063715789784808,8.77966907897848,16.93,0.07431989875355284,null,50,4.694975465500976,30,0.7720023626698169,1.5,19.183019960428737,0.013115276250626973,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","Spare",0,"NA","NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA","NA",null,"SPACE","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA","NA","NA",null,"NA",null,"NA","NA","NA",null,"NA","NA","NA","NA","NA","NA",null,"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air",null,"NA",null,"NA"]
[null,"ID Trim Bulk #1","NA","NA","NA","NA","NA","NA",0.01,0.1,null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA",0,null,"118-MCOR17-PS","NA",1,null,60,"NA",60,141.18785787286933,8.47127147237216,null,80,0.3333333333333333,125,-0.11465474522211014,10,0.18046033970385303,1.4949302598303813,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,14.02044164933054,3,11.073557480225046,11.073557480225046,null,"MCC-01",null,"Power Supply","B118-4306",null,"Air"]
[]
["From SPEAR Operator Log","ID9T-H",1,"Ring","I",0,0.0616365568544102,0,0.01,0.05,null,0.58,0.58,9.41,0,null,"#6","2/C",0.51,800,null,3.83928,0.013547859300000001,null,"07S-ID9TH-PS","NA",1,null,4.41928,"NA",4.41928,9.41,0.0415854248,null,50,10.314060208902808,30,2.1880977683315623,1.5,35.07033010277197,0.007338604376470589,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID10T-H1",1,"Ring","I",0,0.08342602892102335,0,0.01,0.05,null,1.5,1.5,17.98,0,null,"#6","2/C",0.51,800,null,7.33584,0.04946190120000001,null,"06S-ID10TH1-PS","NA",1,null,8.835840000000001,"NA",8.835840000000001,17.98,0.1588684032,null,50,4.658771548602056,30,0.6685205784204672,1.5,8.441776777422787,0.028035600564705887,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID10T-H2",1,"Ring","I",0,0.08356741573033707,0,0.01,0.05,null,2.38,2.38,28.48,0,null,"#6","2/C",0.51,800,null,11.61984,0.12409989120000002,null,"06S-ID10TH2-PS","NA",1,null,13.999839999999999,"NA",13.999839999999999,28.48,0.39871544319999996,null,50,2.5714693882215798,30,0.05337078651685392,1.5,2.762081518491833,0.0703615488,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID11T-H",1,"Ring","I",0,0.08356741573033707,0,0.01,0.05,null,2.38,2.38,28.48,0,null,"#6","2/C",0.51,800,null,11.61984,0.12409989120000002,null,"15S-ID11TH-PS","NA",1,null,13.999839999999999,"NA",13.999839999999999,28.48,0.39871544319999996,null,50,2.5714693882215798,30,0.05337078651685392,1.5,2.762081518491833,0.0703615488,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID11T-V",1,"Ring","I",0,0.0004,0,0.01,0.05,null,0.004,0.004,10,0,null,"#6","2/C",0.51,800,null,4.079999999999999,0.015300000000000001,null,"15S-ID11TV-PS","NA",1,null,4.083999999999999,"NA",4.083999999999999,10,0.04083999999999999,null,50,11.242899118511268,30,2,1.5,35.728697355533804,0.007207058823529414,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID11T-O",1,"Ring","I",0,0.04,0,0.01,0.05,null,0.32,0.32,8,0,null,"#6","2/C",0.51,800,null,3.264,0.009792000000000002,null,"15S-ID11TO-PS","NA",1,null,3.5839999999999996,"NA",3.5839999999999996,8,0.028671999999999996,null,50,12.950892857142858,30,2.75,1.5,51.31584821428572,0.005059764705882354,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID4T-V",1,"Ring","I",0,0.2,0,0.01,0.05,null,2,2,10,0,null,"#6","2/C",0.51,800,null,4.079999999999999,0.015300000000000001,null,"13S-ID4TV-PS","NA",1,null,6.079999999999999,"NA",6.079999999999999,10,0.06079999999999999,null,50,7.223684210526317,30,2,1.5,23.671052631578952,0.010729411764705876,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
["From SPEAR Operator Log","ID7T-V",1,"Ring","I",0.077,0.9640624999999999,0,0.01,0.05,null,12.34,12.34,12.8,0,null,"#6","2/C",0.51,800,null,5.2224,0.025067520000000006,null,"05S-ID7TV-PS","NA",1,null,17.5624,"NA",17.5624,12.8,0.22479872,null,50,1.8469912995945885,30,1.3437499999999998,1.5,5.672635858424817,0.03967036235294119,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"ID Trim Bulk #2","NA","NA","NA","NA","NA","NA",0.01,0.1,null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA",0,null,"118-MCOR18-PS","NA",1,null,60,"NA",60,23.736762007017543,1.4242057204210525,null,80,0.3333333333333333,125,4.266093158074591,10,6.021457544099455,0.2513304212507741,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,2.357142403584737,3,1.8617068240798071,1.8617068240798071,null,"MCC-01",null,"Power Supply","B118-4301",null,"Air"]
[]
[null,"Dipole/QMS Magnets (see above)"]
[" S30731 M313 Rev B 99-07-29","Dipole Trim (Future)",28,"Ring","I",0.077,0.9640624999999999,0,0.01,0.05,null,12.34,12.34,12.8,0,null,"#6","2/C",0.51,820,null,5.35296,0.7018905600000002,null,"Later","NA",null,null,17.69296,"NA",17.69296,12.8,0.226469888,null,50,1.8259827637659274,30,1.3437499999999998,1.5,5.623397102576392,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30731 M313 Rev B 99-07-29","Dipole Trim 3/4",8,"Ring","I",0.058,0.7791208791208791,0,0.01,0.05,null,7.09,7.09,9.1,0,null,"#6","2/C",0.51,820,null,3.80562,0.10135944,null,"MS1-BDMT-PS","NA",1,null,10.89562,"NA",10.89562,9.1,0.09915014199999998,null,50,3.5889999834796003,30,2.2967032967032965,1.5,14.128571374108574,0.017497083882352937,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QDT",28,"Ring","I",0.004,0.17454858125537398,0,0.01,0.05,null,2.870853531617383,2.870853531617383,16.4473037303991,0,null,"#6","2/C",0.51,820,null,6.878262420052904,0.04138861140000002,null,null,"NA",null,null,9.749115951670287,4.133658285662545,10.589258362214922,16.4473037303991,0.08708237428150868,null,50,3.7217659905638243,30,0.8240071741699416,1.5,16.22507008308011,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QFT",28,"Ring","I",0.01,0.27482269503546103,0,0.01,0.05,null,2.1920310216782974,2.1920310216782974,7.976164491784256,0,null,"#6","2/C",0.51,820,null,3.3356319904641754,0,null,null,"NA",null,null,5.527663012142472,5.011571954242637,7.461294246198802,7.976164491784256,0.02975625511464253,null,50,5.701250259024803,30,2.7612062829071675,1.5,49.40956915515475,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QFCT",14,"Ring","I",0.015,0.35920177383592017,0,0.01,0.05,null,2.291025971044414,2.291025971044414,6.378103166302659,0,null,"#6","2/C",0.51,820,null,2.667322744147772,0,null,null,"NA",null,null,4.9583487151921855,6.01122061532827,7.792303591852385,6.378103166302659,0.02485005810599264,null,50,5.416587779290309,30,3.7035927795114025,1.5,59.36203189554201,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QDXT",4,"Ring","I",0.01,0.27468354430379743,0,0.01,0.05,null,3.068843430349616,3.068843430349616,11.172287142747452,0,null,"#6","2/C",0.51,820,null,4.672250483096985,0,null,"118-QMS1-PS","NA",1,null,7.741093913446601,7.019755042290219,10.449951953504808,11.172287142747452,0.05837493192623519,null,50,3.784710994123806,30,1.685215624759041,1.5,24.695961442755216,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QDYT",4,"Ring","I",0.01,0.2755344418052256,0,0.01,0.05,null,3.2809754647055804,3.2809754647055804,11.907678195181461,0,null,"#6","2/C",0.51,820,null,4.979791021224887,0,null,null,"NA",null,null,8.260766485930468,7.481814867858689,11.1453046908545,11.907678195181461,0.06635735082297088,null,50,3.4861940868272976,30,1.5193828308309292,1.5,21.60488071625587,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QDZT",4,"Ring","I",0.01,0.27586206896551724,0,0.01,0.05,null,2.8284271247461903,2.8284271247461903,10.25304832720494,0,null,"#6","2/C",0.51,820,null,4.287824810437106,0,null,null,"NA",null,null,7.116251935183296,6.442180260329631,9.599100380326313,10.25304832720494,0.0492100200485885,null,50,4.208821453985076,30,1.925959094565024,1.5,29.48159701050609,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QFXT",4,"Ring","I",0.017,0.4131274131274132,0,0.01,0.05,null,1.513208511739212,1.513208511739212,3.6628131265463164,0,null,"#6","2/C",0.51,820,null,1.5317884495216694,0,null,null,"NA",null,null,3.0449969612608814,3.912402715342257,4.957711316838191,3.6628131265463164,0.009079585044471076,null,50,9.085298801118535,30,7.190426036909816,1.5,164.20578778139318,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QFYT",4,"Ring","I",0.015,0.3595959595959596,0,0.01,0.05,null,2.5173001410241094,2.5173001410241094,7.000357133746821,0,null,"#6","2/C",0.51,820,null,2.92754935333292,0,null,null,"NA",null,null,5.44484949435703,6.597681163165174,8.554284467270454,7.000357133746821,0.029941523147278177,null,50,4.845024232161672,30,3.285495643554833,1.5,49.09765176680255,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30732 M314 Rev B 99-08-02","QMS - QFZT",4,"Ring","I",0.01,0.27482269503546103,0,0.01,0.05,null,2.1920310216782974,2.1920310216782974,7.976164491784256,0,null,"#6","2/C",0.51,820,null,3.3356319904641754,0,null,null,"NA",null,null,5.527663012142472,5.011571954242637,7.461294246198802,7.976164491784256,0.02975625511464253,null,50,5.701250259024803,30,2.7612062829071675,1.5,49.40956915515475,0,null,null,null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[]
[null,"Skewquad Magnets"]
[" S30735 M315 Rev B 99-08-04","01G-QSS4",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"01G-QSS4-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","02G-QSS3",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"02G-QSS2-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","03G-QSS3",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"03G-QSS2-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","05G-QSS3",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"05G-QSS2-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","07G-QSS2",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"07G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","08G-QSS2",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"08G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","09G-QSS1",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"09G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"SPACE",{"$nulls":22},"SPACE",{"$nulls":38},"NA","NA",null,"Air"]
[null,"Skewquad Bulk PS","NA","NA","NA","NA","NA","NA",0.01,0.1,null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA",0,null,"118-MCOR20-PS","NA",1,null,60,"NA",60,46.46034732500001,2.7876208395,null,80,0.3333333333333333,125,1.690466326598861,10,2.5872884354651484,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,4.885065386037565,3,3.8582987397923882,3.8582987397923882,null,"MCC-01",null,"Power Supply","B118-4406",null,"Air"]
[]
[" S30735 M315 Rev B 99-08-04","10G-QSS4",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"10G-QSS4-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","11G-QSS3",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"11G-QSS2-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","12G-QSS3",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"12G-QSS2-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","14G-QSS2",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"14G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","16G-QSS2",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"16G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","17G-QSS2",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"17G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[" S30735 M315 Rev B 99-08-04","18G-QSS1",1,"Ring","I",0.0047,0.06561491574040874,0,0.01,0.05,null,1.83,1.83,27.89,0,null,"#6","2/C",0.51,825,null,11.7347175,0.11901137130000002,null,"18G-QSS1-PS","NA",1,null,13.5647175,"NA",13.5647175,27.89,0.37831997107500004,null,50,2.6860332697676896,30,0.0756543564001434,1.5,2.96489774446148,0.06676234783676471,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"MCC-01",null,"NA","NA",null,"Air"]
[null,"SPACE",{"$nulls":22},"SPACE",{"$nulls":38},"NA","NA",null,"Air"]
[null,"Skewquad Bulk PS","NA","NA","NA","NA","NA","NA",0.01,0.1,null,"NA","NA","NA","NA",null,"NA","NA","NA","NA",null,"NA",0,null,"118-MCOR21-PS","NA",1,null,60,"NA",60,46.46034732500001,2.7876208395,null,80,0.3333333333333333,125,1.690466326598861,10,2.5872884354651484,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},480,4.885065386037565,3,3.8582987397923882,3.8582987397923882,null,"MCC-01",null,"Power Supply","B118-4401",null,"Air"]
[]
["NA","Long Skewquads (None Powered now but cables pulled)"]
["NA","04G-QSLX Cables Pulled For Future Power",0,"Ring","I",0.0055,0.07344150298889837,0,0.01,0.05,null,1.72,1.72,23.42,0,null,"#6","2/C",0.51,825,null,9.853965,0,null,"04G-QSLX-PS","NA",0,null,11.573965000000001,"NA",11.573965000000001,23.42,0.2710622603,null,50,3.32004071206367,30,0.2809564474807856,1.5,4.533784003497443,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
["NA","06G-QSLX Cables Pulled For Future Power",0,"Ring","I",0.0055,0.07344150298889837,0,0.01,0.05,null,1.72,1.72,23.42,0,null,"#6","2/C",0.51,825,null,9.853965,0,null,"06G-QSLX-PS","NA",0,null,11.573965000000001,"NA",11.573965000000001,23.42,0.2710622603,null,50,3.32004071206367,30,0.2809564474807856,1.5,4.533784003497443,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
["NA","13G-QSLX Cables Pulled For Future Power",0,"Ring","I",0.0055,0.07344150298889837,0,0.01,0.05,null,1.72,1.72,23.42,0,null,"#6","2/C",0.51,825,null,9.853965,0,null,"13G-QSLX-PS","NA",0,null,11.573965000000001,"NA",11.573965000000001,23.42,0.2710622603,null,50,3.32004071206367,30,0.2809564474807856,1.5,4.533784003497443,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
["NA","15G-QSLX Cables Pulled For Future Power",0,"Ring","I",0.0055,0.07344150298889837,0,0.01,0.05,null,1.72,1.72,23.42,0,null,"#6","2/C",0.51,825,null,9.853965,0,null,"15G-QSLX-PS","NA",0,null,11.573965000000001,"NA",11.573965000000001,23.42,0.2710622603,null,50,3.32004071206367,30,0.2809564474807856,1.5,4.533784003497443,0,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},"NA","NA","NA","NA","NA",null,"NA",null,"NA","NA",null,"Air"]
[]
["NA","K1 Injection Kicker",1,"Ring","Later","Later","Later","Later",1,1,null,"Later","Later","Later","Later",null,"AA8481","4-1/C","Later","Later",null,"Later",0,null,"02S-K1-PS","NA",1,null,"12000","NA","12000","0.25",3,null,12000,0,0.25,0,3,0,0.5294117647058822,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},208,11.458090600730845,3,3.9215686274509802,3.9215686274509802,null,"MCC-04",null,"TBD","TBD",null,"Air"]
["NA","K2 Injection Kicker",1,"Ring","Later","Later","Later","Later",1,1,null,"Later","Later","Later","Later",null,"AA8481","8-1/C","Later","Later",null,"Later",0,null,"03S-K2-PS","NA",1,null,"12000","NA","12000","0.25",3,null,12000,0,0.25,0,3,0,0.5294117647058822,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},208,11.458090600730845,3,3.9215686274509802,3.9215686274509802,null,"MCC-04",null,"TBD","TBD",null,"Air"]
["NA","K3 Injection Kicker",1,"Ring","Later","Later","Later","Later",1,1,null,"Later","Later","Later","Later",null,"AA8481","4-1/C","Later","Later",null,"Later",0,null,"04S-K3-PS","NA",1,null,"12000","NA","12000","0.25",3,null,12000,0,0.25,0,3,0,0.5294117647058822,null,"R",null,"NA","NA","NA",null,"NA",{"$nulls":6},208,11.458090600730845,3,3.9215686274509802,3.9215686274509802,null,"MCC-04",null,"TBD","TBD",null,"Air"]
[]
[null,"Spear side of BTS"]
["DellOrco 7/16/01 SS","B7H",1,"BTS","I",0.0464,0.1740648379052369,6.683333333333334,0.1,0.1,null,69.8,69.8,401,0.31010666666666664,null,"2-#4/0","1/C",0.0313,600,null,7.530780000000001,1.5099213900000001,null,"BTS-B7H-PS",62,2,null,77.33078,"NA",77.33078,401,31.009642780000004,null,45,0.16383152995482517,500,0.24688279301745636,22.5,0.45116150867185173,10.944579804705889,null,"R",null,1,600,2,null,62,{"$nulls":6},480,25.66137141168894,3,20.26774037908497,40.53548075816994,null,"MCC-04",null,"Power Supply","B118-1129",null,"Air"]
["DellOrco 7/16/01 SS","B8V",1,"BTS","I",0.0686,0.2082064344648098,6.019666666666667,0.1,0.1,null,75.2,75.2,361.18,0.41294913333333333,null,"2-#4/0","1/C",0.0313,600,null,6.782960400000001,1.224934818636,null,"BTS-B8V-PS",63,2,null,81.98296040000001,"NA",81.98296040000001,361.18,29.610605637272005,null,45,0.09778909618394298,500,0.38435129298410764,22.5,0.5197257547260963,10.450801989625411,null,"R",null,1,600,2,null,63,{"$nulls":6},480,24.503627931927017,3,19.35333701782484,38.70667403564968,null,"MCC-04",null,"Power Supply","B118-1229",null,"Air"]
["DellOrco 7/13/01 SS","Q8",1,"BTS","I",0.45,0.8961538461538462,0.8233333333333334,0.1,0.1,null,44.27,44.27,49.4,0.3705,null,"#6","2/C",0.51,600,null,15.1164,0.37337507999999997,null,"BTS-Q8-PS",64,1,null,59.3864,"NA",59.3864,49.4,2.93368816,null,80,0.3471097759756442,60,0.21457489878542513,4.8,0.6361657198084747,0.5177096752941179,null,"R",null,1,150,2,null,64,{"$nulls":6},208,11.204821577190456,3,3.8348864836601306,3.8348864836601306,null,"MCC-04",null,"Power Supply","B118-1331",null,"Air"]
["DellOrco 7/13/01 SS","Q9",1,"BTS","I",0.45,0.8961538461538462,0.8233333333333334,0.1,0.1,null,44.27,44.27,49.4,0.3705,null,"#6","2/C",0.51,600,null,15.1164,0.37337507999999997,null,"BTS-Q9-PS",65,1,null,59.3864,"NA",59.3864,49.4,2.93368816,null,80,0.3471097759756442,60,0.21457489878542513,4.8,0.6361657198084747,0.5177096752941179,null,"R",null,1,150,2,null,65,{"$nulls":6},208,11.204821577190456,3,3.8348864836601306,3.8348864836601306,null,"MCC-04",null,"Power Supply","B118-1329",null,"Air"]
[]
["NA","01G-TSP1,2,3,4 02G-TSP1,2,3,4                      03G-TSP1,2,3,4 04G-TSP1,2,3,4                    ",1,"Ring","I","NA",0.16,"NA","NA","NA",null,8,8,50,"NA",null,"#4","2/C",0.321,1200,null,19.26,0.24075,null,"118-TSP1-PS",66,1,null,27.26,"NA",27.26,50,1.363,null,40,0.46735143066764484,60,0.2,2.4,0.7608217168011738,0.24052941176470588,null,"R",null,1,150,2,null,66,{"$nulls":6},208,9.016697097192452,1,1.7816993464052286,1.7816993464052286,null,"MCC-04",null,"NA","NA",null,"Air"]
["NA","05G-TSP1,2,3,4 06G-TSP1,2,3,4                           07G-TSP1,2,3,4 08G-TSP1,2,3,4                    ",1,"Ring","I","NA",0.16,"NA","NA","NA",null,8,8,50,"NA",null,"#4","2/C",0.321,1200,null,19.26,0.24075,null,"118-TSP2-PS",67,1,null,27.26,"NA",27.26,50,1.363,null,40,0.46735143066764484,60,0.2,2.4,0.7608217168011738,0.24052941176470588,null,"R",null,1,150,2,null,67,{"$nulls":6},208,9.016697097192452,1,1.7816993464052286,1.7816993464052286,null,"MCC-04",null,"NA","NA",null,"Air"]
["NA","09G-TSP1,2,3,4 10G-TSP1,2,3,4                         11G-TSP1,2,3,4  12G-TSP1,2,3,4 ",1,"Ring","I","NA",0.16,"NA","NA","NA",null,8,8,50,"NA",null,"#4","2/C",0.321,1200,null,19.26,0.24075,null,"118-TSP3-PS",68,1,null,27.26,"NA",27.26,50,1.363,null,40,0.46735143066764484,60,0.2,2.4,0.7608217168011738,0.24052941176470588,null,"R",null,1,150,2,null,68,{"$nulls":6},208,9.016697097192452,1,1.7816993464052286,1.7816993464052286,null,"MCC-04",null,"NA","NA",null,"Air"]
["NA","13G-TSP1,2,3,4 14G-TSP1,2,3,4                             15G-TSP1,2,3,4 16G-TSP1,2,3,4                         17G-TSP1,2,3,4 18G-TSP1,2,3,4                       02S-TSP1  03S-TSP1  04S-TSP1",1,"Ring","I","NA",0.16,"NA","NA","NA",null,8,8,50,"NA",null,"#4","2/C",0.321,1200,null,19.26,0.24075,null,"118-TSP4-PS",69,1,null,27.26,"NA",27.26,50,1.363,null,40,0.46735143066764484,60,0.2,2.4,0.7608217168011738,0.24052941176470588,null,"R",null,1,150,2,null,69,{"$nulls":6},208,9.016697097192452,1,1.7816993464052286,1.7816993464052286,null,"MCC-04",null,"NA","NA",null,"Air"]
[{"$nulls":40},215.31700249862843]
["NA","Ion Pump PS",{"$nulls":22},"Ion Pump PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP01A-PS",{"$nulls":22},"118-IP01A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP01B-PS",{"$nulls":22},"118-IP01B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP02A-PS",{"$nulls":22},"118-IP02A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP02B-PS",{"$nulls":22},"118-IP02B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP03-PS",{"$nulls":22},"118-IP03-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP04-PS",{"$nulls":22},"118-IP04-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP05A-PS",{"$nulls":22},"118-IP05A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP05B-PS",{"$nulls":22},"118-IP05B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP06A-PS",{"$nulls":22},"118-IP06A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP06B-PS",{"$nulls":22},"118-IP06B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP07A-PS",{"$nulls":22},"118-IP07A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP07B-PS",{"$nulls":22},"118-IP07B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP08-PS",{"$nulls":22},"118-IP08-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP09A-PS",{"$nulls":22},"118-IP09A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP09B-PS",{"$nulls":22},"118-IP09B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP10A-PS",{"$nulls":22},"118-IP10A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP10B-PS",{"$nulls":22},"118-IP10B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP11A-PS",{"$nulls":22},"118-IP11A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP11B-PS",{"$nulls":22},"118-IP11B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP12-PS",{"$nulls":22},"118-IP12-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP13A-PS",{"$nulls":22},"118-IP13A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP13B-PS",{"$nulls":22},"118-IP13B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP14A-PS",{"$nulls":22},"118-IP14A-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP14B-PS",{"$nulls":22},"118-IP14B-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP15-PS",{"$nulls":22},"118-IP15-PS",{"$nulls":36},"NA",null,null,"NA"]
["NA","118-IP16-PS",{"$nulls":22},"118-IP16-PS",{"$nulls":36},"NA",null,null,"NA"]
[]
[null,"Total kVA needed",{"$nulls":42},69,null,137,{"$nulls":12},2280.2867699915423]

{"sheet":"Lookup Tables","index":1,"n_rows":47,"n_cols":28,"rows_kept":47,"cut":false,"hidden":false,"merged":[[4,26,4,27],[2,19,2,20],[3,19,3,20],[2,26,2,27],[3,26,3,27],[2,7,2,9],[3,15,3,17],[2,15,2,17],[3,22,3,24],[3,7,3,9],[2,11,2,13],[3,11,3,13]],"flags":["formulas_cached_only"]}
[]
["Multiconductor cables"]
[{"$nulls":7},"90C Cu Multicond Cable",null,null,null,"90C Cu 1/C Cable",null,null,null,"75C Tinned Cu ",null,null,null,"Transductor",null,null,"Power Supply",null,null,null,"CB Ratings"]
["NEC Article 318-11(a) for cables in cable trays.",{"$nulls":6},"NEC 310-16",null,null,null,"NEC 310-17",null,null,null,"NEC Chap 9, Table 8",null,null,null,"Sizes",null,null,"Vin, Phase & Power Density",null,null,null,"NEC"]
[{"$nulls":8},"Conductor","AWG",null,null,"Conductor","NEC",null,"NEC",null,"Ohms/",{"$nulls":4},"Vs  Po",null,null,null,"240-6(a)"]
[" Multiconductor cables <#1/0 AWG use Table 310-16.",{"$nulls":6},"Amps","Diameter","Size",null,"Amps","Diameter","Size",null,"Size",null,"1000 ft",null,"PS Io","XDCR",{"$nulls":5},"PS","Trip"]
[{"$nulls":7},0,0.073,"#14",null,0,0.073,"#14",null,"#16",null,5.29,null,"Amps","Amps",null,"KW","Volts","Phases",null,"Amps","Amps"]
["Cable quantity derating factors only apply to multiconductor",{"$nulls":6},25,0.073,"#14",null,10,0.073,"#14",null,"#14",null,3.26,null,0,0,null,0,208,1]
["cables of more than 3 current currying conductors.",{"$nulls":6},30,0.092,"#12",null,20,0.073,"#14",null,"#12",null,2.05,null,150,150,null,3,208,1]
[{"$nulls":7},40,0.116,"#10",null,30,0.092,"#12",null,"#10",null,1.29,null,300,600,null,5,208,3,null,0,15]
["Use ambient derating factor of 0.87 for max 110F ambient.",{"$nulls":6},55,0.146,"#8",null,55,0.116,"#10",null,"#8",null,0.809,null,600,600,null,9.9,480,3,null,15,20]
[{"$nulls":7},75,0.184,"#6",null,80,0.146,"#8",null,"#6",null,0.51,null,1000,1000,null,15,480,3,null,20,25]
[{"$nulls":7},95,0.232,"#4",null,105,0.184,"#6",null,"#4",null,0.321,null,2000,2000,null,20,480,3,null,25,30]
["Single conductor cables",{"$nulls":6},110,0.26,"#3",null,140,0.232,"#4",null,"#3",null,0.254,null,3000,3000,null,100,480,3,null,30,35]
[{"$nulls":7},130,0.292,"#2",null,165,0.26,"#3",null,"#2",null,0.201,{"$nulls":4},2400,480,3,null,35,40]
["NEC Article 318-11(b) for cables in cable trays.",{"$nulls":6},150,0.332,"#1",null,190,0.292,"#2",null,"#1",null,0.16,{"$nulls":4},4000,480,3,null,40,45]
[{"$nulls":7},170,0.373,"#1/0",null,220,0.332,"#1",null,"#1/0",null,0.127,{"$nulls":8},45,50]
[" Single conductor cables =>#1/0 AWG use Table 310-17and",{"$nulls":6},195,0.419,"#2/0",null,260,0.373,"#1/0",null,"#2/0",null,0.101,{"$nulls":8},50,60]
[{"$nulls":7},225,0.47,"#3/0",null,300,0.419,"#2/0",null,"#3/0",null,0.0797,{"$nulls":8},60,70]
["(1) => 600kcmil, 75% of basic ampacity.",{"$nulls":6},260,0.528,"#4/0",null,350,0.47,"#3/0",null,"#4/0",null,0.0626,{"$nulls":8},70,80]
[{"$nulls":7},290,0.575,"#250",null,405,0.528,"#4/0",null,"#250",null,0.0535,{"$nulls":8},80,90]
["(2) #1/0 through 500kcmil use 65% of basic amapcity.",{"$nulls":6},320,0.63,"#300",null,455,0.575,"#250",null,"#300",null,0.0446,{"$nulls":8},90,100]
[{"$nulls":7},350,0.681,"#350",null,505,0.63,"#300",null,"#350",null,0.0382,{"$nulls":8},100,110]
["Use ambient derating factor of 0.87 for max 110F ambient.",{"$nulls":6},365,0.703,"#373",null,570,0.681,"#350",null,"#373",null,0.0359,{"$nulls":8},110,125]
[{"$nulls":7},380,0.728,"#400",null,591,0.703,"#373",null,"#400",null,0.0331,{"$nulls":8},125,150]
[{"$nulls":7},430,0.813,"#500",null,615,0.728,"#400",null,"#500",null,0.0265,{"$nulls":8},150,175]
[{"$nulls":7},475,0.893,"#600",null,700,0.813,"#500",null,"#535",null,0.0265,{"$nulls":8},175,200]
[{"$nulls":7},520,0.964,"#700",null,780,0.893,"#600",null,"#600",null,0.0223,{"$nulls":8},200,225]
[{"$nulls":7},535,0.998,"#750",null,810,1.056,"2-#4/0",null,"#700",null,0.0189,{"$nulls":8},225,250]
[{"$nulls":7},555,1.03,"#800",null,910,1.15,"2-#250",null,"#750",null,0.0176,{"$nulls":8},250,300]
[{"$nulls":7},585,1.09,"#900",null,855,0.964,"#700",null,"#800",null,0.0166,{"$nulls":8},300,350]
[{"$nulls":7},615,1.15,"#1000",null,885,0.998,"#750",null,"#900",null,0.0147,{"$nulls":8},350,400]
[{"$nulls":7},665,1.29,"#1250",null,920,1.03,"#800",null,"#1000",null,0.0132,{"$nulls":8},400,450]
[{"$nulls":7},705,1.41,"#1500",null,985,1.09,"#900",null,"#1250",null,0.0106,{"$nulls":8},450,500]
[{"$nulls":7},735,1.52,"#1750",null,1055,1.15,"#1000",null,"#1500",null,0.00883,{"$nulls":8},500,600]
[{"$nulls":7},750,1.63,"#2000",null,1200,1.29,"#1250",null,"#1750",null,0.00756,{"$nulls":8},600,700]
[{"$nulls":11},1325,1.41,"#1500",null,"#2000",null,0.00662,{"$nulls":8},700,800]
[{"$nulls":11},1445,1.52,"#1750",null,"2-#4/0",null,0.0313,{"$nulls":8},800,1000]
[{"$nulls":11},1560,1.63,"#2000",null,"2-#250",null,0.02675,{"$nulls":8},1000,1200]
[{"$nulls":11},1600,null,"2-#600",null,"2-#500",null,0.01325,{"$nulls":8},1200,1600]
[{"$nulls":11},1700,null,"2-#700",null,"1\"AL",null,0.03,{"$nulls":8},1600,2000]
[{"$nulls":11},1840,null,"2-#800",null,"2-1\"AL",null,0.015,{"$nulls":8},2000,2500]
[{"$nulls":11},1970,null,"2-#900",{"$nulls":12},2500,3000]
[{"$nulls":26},3000,4000]
[{"$nulls":26},4000,5000]
[{"$nulls":26},5000,6000]
[{"$nulls":26},6000]